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SZ-6  Vibration Sensor
Manual
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Xiamen Kehao Automation Co., Ltd 

Add: S305, Weiye Building, Huoju 
    Hi-tech District, Xiamen, China 361006. 

Tel: 0086-592-3191333
Website: http://www.kehaoauto.com

1). General                                             
SZ-6 integrative Vibration Sensor, integrating the traditional vibration sensor and the accuracy measuring circuit together, not only achieve “sensor + transmitter” mode Acceleration measurement system function, but also achieve economic but high accuracy Acceleration measure system. The transmitter can connect directly with PLC, DCS or other systems. Mounted on the bearing cover of rotating machines, the transmitter is an ideal choice for steam turbine, compressors, motors, blower, fans, water pump etc to measure Acceleration.The transmitter can be used widely in heating and power plant, cement plant, machine plant, blower plant, paper made plant, coal mine machine etc.
Mounting method: vertical or horizontal mounted on the measured vibrating point
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2). Specification                                      
1. Sensitivity: 
20mv/mm/s±0.3%  30mv/mm/s±0.3%  50mv/mm/s±0.3%  

2． Frequency Response: 10-1000Hz 

3． Measuring Range
2mm(P-P)Other

4． Signal Output: standard current 4-20mA (default when order) or RS485

5． Output Impedance: ≤500              
6． Power supply: DC24V

7． Max acceleration: 200g                 
8． Measurement Direction: vertical or horizontal

9． Mounting method: vertical or horizontal mounted on the measured vibrating point
10. Mounting thread: Thread（M8*1.25,or M10*1.5,or M10*1.0）
11. Ambient Temperature: -40℃ to 85℃, 

Relative humidity: ≤90%

12. Size: φ39×82mm,           

13. Weight: About 250g
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3）Temperature Curve Parameters
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4）.  Frequency response curve parameters
5）Size
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6）Wiring diagram
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Remark：This product has anti-inversion function inside, so there is no positive or negative difference between the lead wire, that is, +24V to connect one line at will, 4-20mA to connect another line.

7）Order code
SZ-6 Selection of Piezoelectric Integrated Vibration Sensor
SZ-6-□-C□□-D□□-E□□-F□□
	
   Type
	C  measuring range
	D  Thread
	E Wire length

	B

(Non explosion-proof）
F

(explosion-proof）


	mV:

01: 10.0mv/mm/s
02: 20.0mv/mm/s
03: 30.0mv/mm/s
05: 50.0mv/mm/s
.........


	11: M8*1.25

12: M10*1.0

13: M5*0.8

14: 1/4~28

15:Other


	01: 1m

02: 2m

03: 3m

.............




For example：SZ-6 -C（mV02）-D （11）-E（02）-F(4)

Meaning: Type of measurement - - non-explosion-proof, 

Measuring range - - 20.0mv/mm/s
Installation mode - - M8 *1.25
Cable length - - 2 meters
Output - - 4-20mA
